AGENDA ITEM  8.0

TECHNICAL

ELECTRICAL SAFETY POLICY

February 2022

February 2027

| Policy on : | Electrical safety in domestic properties |
| --- | --- |
| Compliant with Charter : | 5. Repairs, maintenance and improvements Tenants’ homes are well maintained, with repairs and improvements carried out when required, and tenants are given reasonable choices about when work is done. 6. Estate Management Tenants live in well- maintained neighbourhoods where they feel safe |
| Compliant with Tenant Participation Strategy: | The level of consultation is information provision by placing the policy on our web site as it deals with building standards and compliance with legislation. |
| Compliant with Equal Opportunities : | Yes |
| Compliant with Business Plan : | Yes |

| Date Approved: Date for Review : | February 2027 |
| --- | --- |

| Responsible Officer: | Head of Technical |
| --- | --- |

Contents

- Introduction

- Risk

- Legislation

- The Association’s Responsibilities

- The Tenants’ Responsibilities

- The Contractor’s Responsibilities

- Frequency of Inspections & Testing

- Forced Access

- Equal Opportunities

- Complaints

- Review

1.0 Introduction

1.1 The purpose of this Policy is to set out specific guidelines to enable Paisley Housing Association to be assured that the electrical safety of fixed electrical installations are inspected and maintained at appropriate frequencies to minimise the risk of fire, injury and / or death.

1.2 The policy applies to all of the Association’s domestic properties.  It is supported by a Procedure on Electrical Safety.

2.0 Risk

2.1 By having a written detailed Electrical Safety Policy and Procedure the Association is able to ensure that a uniform and professional approach is adopted throughout the organisation and the service delivered is compliant with law, best practice and internal policy.

2.2 The risk of not having this Policy in place is that systems are not serviced in accordance with legislation and good practice guidance.

2.3 The main hazards of electrical systems are:

- contact with exposed live parts

- faults which could cause fires

- fire or explosion where electricity could be the source of the ignition

3.0 Legislation

3.1 Paisley Housing Association is committed to ensuring the safety of its residents with regards to electrical installations in our properties.

It will comply with all relevant legislation and regulations including:

- Scottish Government Fire safety regulations requiring an interlinked smoke detection system in all domestic properties  by February 2022

- From March 2022 that  a Periodic Inspection Report is mandatory

- The Housing (Scotland) Act 2006 which requires an electrical installation in a rented property to be ‘in a reasonable state of repair and proper working order at the start of the tenancy and at all times during the tenancy’. Electrical installation is defined in Chapter 14 of the Housing (Scotland) Act 2006 as ‘the electrical wiring within the property and associated components and fittings, but excludes equipment and appliances.’

3.2  We are committed to complying with the 18th Edition of the IET (Institution of Engineering and Technology) Wiring Regulations (BS 7671:2019) which came into effect on 1st January 2019. All domestic wiring installations must now be designed, constructed, inspected, tested and certificated to meet the requirements of BS 7671: 2019.

4.0 The Association’s Responsibilities

4.1 Fixed Electrical Installations

4.1.1 An electrical installation is made up of all the fixed electrical equipment that is supplied through the electricity meter. It includes the cables that are usually hidden in the fabric of the building (walls and ceilings), accessories (sockets, switches and light fittings), and the consumer unit (fuse box) that contains all the fuses or circuit-breakers.

4.1.2 The Association aims to ensure that its electrical installations should have:

- sufficient sockets for the number of portable appliances likely to be used, in order to minimise the use of multi-socket adapters

- covers in place to ensure that fingers cannot come in contact with live parts

- residual current device (RCD) protection where appropriate

- satisfactory earthing arrangements

- satisfactory bonding arrangements

- enough circuits to avoid danger and minimise inconvenience in the event of a fault cables that are correctly selected in relation to their associated fuse or circuit-breaker

4.2 A Periodic Inspection is an inspection on the condition of an existing electrical

installation, to identify (in order of priority) any deficiencies against the National

Standard, BS 7671, for the safety of electrical installations. Its purpose is to:

- reveal if any of the electrical circuits or equipment are overloaded

- find any potential electrical shock risks and fire hazards in the electrical

installation

- identify any defective DIY electrical work

- highlight any lack of earthing or bonding

Tests are also carried out on the electrical installation to check that it is safe.

4.3 For tenanted properties a Periodic Inspection Report (PIR) will be carried out at 5 yearly intervals by a competent electrician. A copy of this will be given to the current tenant. The overall outcome stated on the report should be a 'Satisfactory', any Code 1 or Code 2 issues will be rectified. A code FI will require further investigation before an outcome of satisfactory can be obtained.

4.4 When a void property is being made ready to let the Association will carry out a Periodic Inspection Report (PIR) to ensure the safety of an incoming tenant. This will include checking that all fire detection equipment is still compliant.

4.5 New tenants will receive a copy of the Periodic Inspection Report for the property. The overall outcome stated on the report will be 'Satisfactory', with any Code 1 or Code 2 or Code FI issues having been rectified.

4.6 All properties will be let with a minimum standard of electrical fittings and fixtures, in line with our property letting standard.

4.7 New Electrical Work

4.7.1 The Association will comply with the Building (Scotland) Regulations 2004 for electrical safety. Mandatory standard 4.5 states that: ‘every building must be designed and constructed in such a way that the electrical

installation does not: a) threaten the health and safety of the people in, and around, the building b) become a source of fire’

4.7.2 From 2016 in accordance with Reg 421.1.201 stock that is rewired will have to have new consumer units and similar switchgear enclosure, either manufactured in non-combustible material, or be enclosed in a cabinet or enclosure constructed of non- combustible material.

4.8 Portable Appliances

4.8.1 Paisley Housing Association will be responsible for any hard wired appliances that we own in a tenanted property in accordance with The Electrical Equipment (Safety) Regulations 1994. There are also some portable appliances which are also covered by this policy:

- in general needs communal areas Oliphant Court laundry

- in some mobility tenanted property,

- in some general needs tenanted property where there are no drying facilities

Portable appliances in office accommodation are not covered by this policy.

4.8.2 The Electrical Equipment (Safety) Regulations require us to ensure that the appliances are safe when first supplied. Although there is no specific requirement for portable appliance testing to be carried out in RSL accommodation, landlords are required to take reasonable steps to ensure that appliances such as  washing machines provided as part of the tenancy agreement are safe.

4.8.3 This will be done by means of ‘Portable appliance testing’ to ensure equipment is safe for continued use and will be carried out annually in addition to the 5 YEARLY PIR in tenanted property.

4.8.4PHA appliances in empty property will be PAT tested before re-let in addition to the PIR testing. Appliances not provided and maintained by PHA will be removed from empty properties.

4.9 Paisley Housing Association will retain a copy of the Electrical Installation Condition Report for 6 years. As noted above a copy of the most recent report will be issued to the tenant before a tenancy starts. If an inspection is carried out during a tenancy, a copy relating to that inspection will also be given to the tenant.

4.10 Tenants will be issued with information leaflets on electrical safety and advised to report any electrical faults immediately. They will be informed of any electrical items which are prohibited within their home.

5.0 Tenant Responsibilities

5.1 To undertake fixed installation inspection and testing, it is necessary to temporarily de-energise the electrical supply to the property.

5.2 All tenants properties where Electrical Inspection and Testing is to be carried out, shall be written to informing them that the electrical installation will require temporary de- energising and that the Association accepts no responsibility for any loss or damage resulting from this.

5.3 Accordingly, the tenant should:

- Identify any requirement to save IT software and action this before the

start of any electrical operations

- Make their own contingency arrangements for the absence of electrical supplies e.g. to freezers/ fridges

- Make sure appropriate access and relocation/removal of any obstacles has been done before the contractor arrives.

5.4 Paisley Housing Association is not responsible for the safety of residents’ cookers or fixed or portable electrical appliances not provided by the Association; or installations which have been installed without our prior approval.

5.5 If any installation has been undertaken without our permission, and is found to be defective at PER inspection, the contractor will terminate the supply and make recommendations for the required rectification works.

5.6 Residents are responsible for the cost of any repairs relating to damage they have caused with faulty self-installed appliances and wiring.

5.7 Under the terms of the Scottish Secure Tenancy Agreement Section 5 tenants must allow access to their property to carry out maintenance or safety checks. Should this be refused, the Association will take action following formal notification to force access in order to carry out mandatory safety work.

5.8 Residents are responsible for portable appliances that they own.

5.9 The Association will recommend to outgoing residents doing a mutual exchange that they should not gift any appliances to the next resident without a PAT test.

6.0 The Contractor’s Responsibilities

6.1 Only suitably competent & experienced contractor may carry out safety checks.

6.2 Contractors will comply with our Contractor Code of Conduct. Contractors appointed to undertake Periodic Inspection and Testing of Electrical

Installations will also be required to conform in full with the requirements of this

Policy.

6.3 All appointed electrical contractors shall be registered with the NICEIC (or equivalent) and shall be registered under a recognised Domestic Installer self-certification scheme in compliance with Part P of the Building Regulations.

6.4 The contractor undertaking electrical work will work in accordance with the Health and Safety at Work Act 1974, the Electricity at Work Regulations 1989 and all other current relevant legislation and approved codes of practice, specifically

complying with British Standard 7671: 2019 (IET Wiring Regulations)

6.5 Only skilled persons as defined by BS 7671 2019 (Requirements for Electrical Installations) including all current amendments will be authorised to carry out Inspection and Testing. A person shall be deemed skilled to carry out the appropriate Inspection and Testing only if she/he has sufficient knowledge and experience of the test equipment, the installation being tested and testing procedures. All Electricians should have successfully completed City and Guilds 2382 (17th Edition) City and Guilds 2391 (Inspection, Testing and Certification of Electrical Installations).

6.6 Except for undertaking unforeseen emergency repairs whilst carrying out the Inspection and Testing regime, no repairs or rectification works shall be started without first obtaining the correct authority from an appointed member of Paisley  Housing Associations staff.

6.7 All new installations shall be provided with an Electrical Installation Certificate complete with a Schedule of Inspections and Test Results. The documents shall be suitably completed and in full compliance with BS 7671: (2019) Requirements for Electrical Installations., Guidance Note 1 (Selection and Erection) and all current amendments.

6.8 Records shall be provided in full accordance with BS 7671 20198 Requirements for Electrical Installations and Guidance Note 3 (Inspection and Testing) including all amendments. Original Inspection certificates must be provided to Paisley Housing Association.

6.9 Test equipment shall comply with the requirements of BS 7671 2019 Requirements for Electrical Installations and Guidance Note 3 (Inspection and Testing). Including all amendments.

6.10 All contractors and subcontractors working on behalf of Paisley Housing Association must comply with our requirements for PAT testing e.g. cleaners supplying their own equipment, and contractors providing temporary equipment such as dehumidifiers or heaters to tenants.

6.11 The Contractor will ensure that the periodic inspection takes into account all relevant circumstances including:

- adequacy of earthing and bonding,

- suitability of the switchgear and control gear, for example, old fuse boxes with

double-pole fusing and/or wooden enclosures, which are likely to need

replacing,

- serviceability of accessories and light fittings, for example, older round-pin sockets, sockets mounted on skirting boards, round pattern lighting switches and braided flexible cords connecting ceiling roses to lamp holders, which may require replacement due to unsuitability or deterioration,

- types of wiring systems and their condition, for example, cables coated in black rubber (phased out in the 1960s) which may be in poor condition and need replacing,

- extent of any wear and tear, damage or other deterioration of other parts of the  installation

- presence of adequate identification and notices

- changes in use of the premises which have led to, or might lead to, deficiencies in the installation.

6.12 Periodic inspection report observations and recommendations

6.12.1 The electrician carrying out the inspection will provide a periodic inspection report (PIR) to record the findings of the inspection. In addition to the main body of the report, which will identify departures from the requirements of BS 7671 and provide an overall assessment of the suitability of the installation for continued use, the report should be accompanied by schedules of inspection and test results.

6.12.2 The overall assessment section(s) of the report should describe the overall condition as either 'satisfactory', in which case no immediate remedial work is required, or 'unsatisfactory' which means remedial work is required to make the installation safe to use.

6.12.3 The observations and recommendations should take due account of the results of the inspection and testing. They should be based on the requirements of the issue of BS 7671 current at the time of the inspection, not on the requirements of an earlier standard current at the time the installation was constructed.

The observation(s) should be provided in an accurate and easily-understandable manner.

6.12.4 Any relevant observation recorded by the electrician in the ‘observations and recommendations’ section of the report should be accompanied by a recommendation code to indicate the action needed. Further detail on the codes is given below.

Code C1 Danger Present

Code C2 Potentially dangerous

Code C3 Improvement recommended

Code FI Further investigation required

6.12.5 The electrician will also give a summary of the inspection in the report, which will give a clear indication of the condition of the electrical installation, taking into account all relevant circumstances. Once the necessary remedial work has been completed, an appropriate certificate should be issued to confirm that the remedial work has been carried out in accordance with BS 7671.

6.12.6 Code 1

Where a real and immediate danger is observed that puts the safety of

those using the installation at risk, Recommendation Code 1 (requires

immediate attention) must be given. The Association should be

advised to take action without delay to remedy the observed deficiency in the

installation, or to take other appropriate action (such as switching off and isolating the affected parts of the installation) to remove the danger.

Where a Recommendation Code 1 is given, the Association will be advised immediately, by phone and e-mail, that urgent work is necessary to remedy the deficiency. This action is necessary to satisfy the duties imposed on the inspector and others by the Health and Safety at Work etc. Act 1974 and the Electricity at Work Regulations 1989.

6.12.7 Code 2

A Code 2 is to be used to indicate that the observed deficiency requires action to

remove potential danger. The Association should be advised that, whilst the safety of those using the installation may not be at immediate risk, urgent remedial action should be taken to improve the safety of the installation.

6.12.8 Code 3

A code 3 is to be used to indicate that certain items have been identified as not

complying with the requirements of the current issue of BS 7671, but that the users of the installation are not in any immediate or potential danger as a result. Careful consideration should be given to the safety benefits of improving those aspects of the installation.

6.12.9 Code FI

This is used where there is a need for further investigation because the  inspector considers that this may reveal danger or potential danger that due to the agreed extent or limitations of the inspection/testing could not be fully identified at the time.

7.0 Frequency of Inspection and Testing

7.1 The frequency of periodic inspection and testing should be determined taking into account:

- the type of installation

- its use, the extent of wear and tear, and operation and/or level of misuse (e.g. vandalism)

- the frequency and quality of maintenance

- the damage and/or deterioration found at the time of the inspection

7.2 Guidance Note 3: Inspection and Testing IEE indicates a suggested frequency of 10 years for a PIR for domestic properties from the date of the first installation, then 5 yearly, but with an inspection also carried out at change of occupancy. These frequencies should be increased if the history indicates signs of progressive deterioration.

7.3 However the requirement for a PIR becomes mandatory from March 2022. The Associations stock will be subject to a full Periodic Inspection and Test at the following frequencies:

- Newbuild/improved-first inspection to be carried out by Association 10 years after coming off site, thereafter every 5 years

- Properties that have been fully rewired as part of a planned maintenance programme- first inspection to be carried out by Association 10 years after completion of planned maintenance work, thereafter every 5 years

- All other general needs stock to be inspected every 5 years.

- If applicable following rectification of damage e.g. insurance claim works

- At change of occupancy i.e. a void or mutual exchange

8.0  Forced Access

8.1 The Association’s actions to secure access to a property in the event of no-access are outlined in its Procedure on Electrical Safety.

8.2 The Association’s contractor will absorb the cost of 1 arranged visit and will charge further visits to the Association i.e. 2nd no access. The Association will pass on these costs to the tenant in the form of a recharge.

8.3  However since it is now mandatory to have a PIR the Association will carry out the same formal process for electrical safety as it does for gas safety. This is one formal letter after 2 attempts to gain access, and then a formal notice of forced access where there has been no co-operation in allowing access.

8.4 Where Housing Management staff believes a property has been abandoned, and serve the appropriate Notice, they will inform Technical staff in order that efforts to secure access can be coordinated.

9.0 Equal Opportunities

9.1 The Association promotes equal opportunities and will not discriminate between persons on grounds of gender or marital status, on racial grounds, or on grounds of disability, age, sexual orientation, language or social origin, or of other personal attributes, including beliefs or opinions, such as religious beliefs or political opinions.  See our Equalities and Diversity Policy.

10.0 Complaints procedure

10.1 The Association aims to ensure that the service provided to residents is of the highest quality. If this is not the case, a Complaints Policy and Procedure is in place to allow all residents or affected parties to state their grievance. The Scottish Public Services Ombudsman is the final stage of this process.

11.0 Review

11.1 This Policy will be reviewed five years from the date of approval.

11.2 Consideration will be given to any changes in legislation, good practice or operational changes which may affect the content.